Three-Phase High-Voltage Power Supply for the Electrical Precipitator

Operating Instructions

(Version No.: ZC32-2015A)

Fujian Longking Co., Ltd.

January 2015

Proper Use:

1.	The mounting and operation of the device must be carried out as per the requirements of the instructions. Only the competent persons are allowed to mount and operate this equipment.

2. To ensure the equipment safety and personal safety, the electrostatic precipitator must be equipped with the grounding system in strict accordance with the national standards or industrial standards. The plant power grid ground, high voltage control cabinet ground, rectifier transformer ground and the electrostatic precipitator anode shall be connected together and grounded at the same position. The control cabinet shell, transformer shell and body shell must also be reliably connected with the grounding terminal. The grounding resistance shall not be measured less than once a year to ensure that the grounding resistance of the system is less than 2.0Ω.

3. Before the unloaded testing, the insulation inspection shall be carried out for the rectifier transformer with 2500V megohmmeter first; the trail power-on testing shall be carried out for the high-voltage control cabinet with the fictitious load.

4. Before the official operation of the equipment, the high-voltage safety interlock, operating procedures, high voltage risk warning signs must be improved.

5. During the equipment debugging and maintenance, the operation must be carried out as per the specifications, and the hot unplug the plug-in with electricity is forbidden.

6. During the operation of the equipment, to ensure the equipment and personal safety, the operation of the high-voltage isolating switch with the electricity is forbidden.

All Rights Reserved:

1. All the copyrights belong to our company. Without expressed written permission, this manual or partial content therein shall not be duplicated or reproduced. The violator shall be responsible for the losses caused.

2. Our company reserves the right of final interpretation.

Disclaimer:

1. The contents contained in the instructions will be changed without notice due to product improvement. Please understand at that time.

2. We have checked that the contents of the instructions are consistent with the hardware in the related contents. We cannot guarantee the complete consistency due to the errors which are inevitable. Please contact us if there is any unclear or incorrect content, and your valuable comments are welcome.